## Plumbing Report
PLUMBING DEFICIENCY INSPECTION AND RISER PRESSURIZATION REPORT
Spark Hotel ¦ 6950 Nova Way, Manassas, VA
Company: Remington Construction LLC |  |  | Activity period: 2026-07-08 to 2026-07-13
Based on ZonePillar Activity Log and field observations by Remington
This report identifies observed deficiencies and code-review items. Final violation determinations remain subject to field measurements, approved construction documents, exact equipment listings/manufacturer instructions and the Authority Having Jurisdiction.
EXECUTIVE RECOMMENDATION
Based on recurring leaks, non-holding valves, damaged handles, difficult operation, oxidation and restricted service access, replacement of all riser isolation valves is highly recommended. There is a good amount of minor repairs should be performed (angle stop valve replacement 100%, new p-trap and drain pipes, leaking toilet. toilet tanks, clogged drain pipes should be replaced) Each riser valve should be repaired as required and pressure-tested. The water-heater installations should receive a complete code and manufacturer-instruction inspection before acceptance or continued operation, RC is working on obtaining a permit to perform inspection of the water heaters to get final list of violations. Missing water piping insulation must be installed to meet code requirements and reduce mold growths.
Summary Metric | Count |  | REPORT SCOPE
Existing activity-log issues | 29 |  | Corrective work should be sequenced by actual field conditions, active leakage, operational impact, approved project documents and direction from the Authority Having Jurisdiction.
CONSOLIDATED PLUMBING DEFICIENCIES FROM ACTIVITY LOG
Issue Type | Location | Component | Detailed Condition / Finding | Recommended Corrective Action
Leak/Mold | 1st Floor - Lobby | Copper piping | Copper pipe leak caused moisture damage/mold at the lobby ceiling. Ceiling was opened during investigation. Riser needs to replaced and insulation installed. | Repair the leaking copper piping, dry and remediate the affected area, and verify the repair under pressure Riser needs to replaced and pipe insulation installed..
Leak | 1st Floor - Riser 6 | 1-1/4 in. valve/pipe connection | Leak reported at the 1-1/4 in. valve and adjoining pipe connection. | Replace the defective valve/connection and pressure-test the assembly.
Leak | 2nd Floor - Riser 1 | Toilet | Toilet leak reported. | Toilet tank and connection to be replaced
Leak | 3rd Floor - Riser 1 | Sink/p trap | /P-trap leak under the sink | Replace sink p trap
Leak | 2nd Floor - Riser 2 | Toilet | Toilet leak reported. | Repair and perform operational/leak test. Replace toilet with a tank
Leak | 2nd Floor - Riser 3 | Toilet | Toilet leak reported. | Repair and perform operational/leak test. Replace toilet with a tank
Drainage | 3rd Floor - Riser 3 | Sink | Sink reported clogged. | Clear obstruction (drywall and trash), clean/replace drainage piping, and verify full flow.
Leak | 2nd Floor - Riser 4 | Toilet | Toilet leak reported. | Repair and perform operational/leak test. Replace toilet with a tank
Leak | 2nd Floor - Riser 10 | Toilet valve | Leak reported at toilet valve. | Replace angle stop valves, possible extension of 1/2 copper pipe needed.
Leak | 2nd Floor - Riser 19 | Toilet | Toilet leak reported. | Repair and perform operational/leak test. Replace toilet with a tank
Leak | 2nd Floor - Riser 20 | Toilet | Toilet leak reported. | Repair and perform operational/leak test. Replace toilet with a tank
Leak | 3rd Floor - Riser 20 | Toilet | Toilet leak reported. | Repair and perform operational/leak test. Replace toilet with a tank
Leak | 2nd Floor - Riser 22 | P-trap | P-trap leak reported | Replace p trap.
Leak | 2nd Floor - Riser 23 | P-trap | P-trap leak reported. A related first-floor note references leakage from the third-floor P-trap; exact location should be field-verified. | Field-verify affected fixture/floor (room TBD in zonepillar), repair the P-trap, and test.
Leak | 3rd Floor - Riser 25 | Toilet | Toilet leak reported. | Repair and perform operational/leak test. Replace toilet with a tank
Leak | 3rd Floor - Riser 29 | Toilet | Toilet leak reported. | Repair and perform operational/leak test. Replace toilet with a tank
Leak | 3rd Floor - Riser 30 | Toilet | Toilet leak reported. | Repair and perform operational/leak test. Replace toilet with a tank
Valve | 2nd Floor - Riser 28 | Valve below sink | Valve below sink is not holding. | Replace the valve and pressure-test.
Valve | 1st Floor - Riser 1 - Gym | Riser isolation valves | Valves were specifically noted as needing replacement; no active leak was observed. | Replace all associated riser valves and verify isolation.
Valve | 1st Floor - Riser 2 | Riser valves | Valves are in fair condition and difficult to operate. | Replace riser valves rather than relying on continued operation of deteriorated valves.
Valve | 1st Floor - Riser 3 | Hot-water valve | Valves are in fair condition; hot-water valve is difficult to operate. | Replace the affected riser valves and verify operation.
Valve | 1st Floor - Riser 11 | Riser valves | Valves are in fair condition and installed too close to the wall, restricting service access. | Replace/reconfigure valves to provide reliable operation and adequate access.
Valve | 1st Floor - Riser 12 - former Room 111 | Riser valves | Valves are in fair condition. Room was noted as demolished; no leak was reported. | Replace riser valves during renovation while access is available.
Valve | 1st Floor - Riser 13 | Right-side valve handle | Right-side valve handle is nonfunctional. | Replace the valve/handle assembly and verify shutoff.
Valve | 1st Floor - Riser 18 | Left-side valve handle | Left-side handle is crooked (bended) | Replace damaged valve and verify operation.
Valve | 1st Floor - Riser 29 | Left-side valve handle | Left-side handle is crooked(bended). | Replace damaged valve/ and verify operation.
Valve | 2nd Floor - Riser 22 | Valve | valve requiring change/replacement. | Field-verify the specific valve and replace it.
Service interruption | 3rd Floor - Riser 17 | Toilet water supply | Toilet reported without water. | Trace supply, confirm valve positions/pressure, restore service, and test.
Identification | 1st Floor - Main mechanical room | Piping and valves | Oxidation was observed on some piping and valves. | Replace damaged/old/oxidated components